## Water Treatment Cost Estimates
CSP2 Financial Assurance Calculations
Average Closure Costs for ARD Water Treatment Facilities
24 April 2003
| Influent Water Quality | [14 empty] | Target Effluent Water Quality / Permit Requirements
Facility | Average Flow Rate (gpm) | Maximum Flow Rate (gpm) | pH (su) | TDS (mg/L) | TSS (mg/l) | Sulfate (mg SO4/L) | Diss. Al (mg/L) | Diss. As (mg/L) | Diss. Cd (mg/L) | Diss. Cu (mg/L) | Total Fe (mg/L) | Diss. Pb (mg/L) | Total Mn (mg/L) | Diss. Ni (mg/L) | Diss. Zn (mg/L) | Average Flow Rate (gpm) | pH (su) | TDS (mg/L) | TSS (mg/l) | Sulfate (mg SO4/L) | Nitrate + Nitrite as N (mg/L) | Diss. Al (mg/L) | Total As (mg/L) | Diss. Cd (mg/L) | Total Cd (mg/L) | Diss. Cu (mg/L) | Total Cu (mg/L) | Total Cyanide (mg/L) | Total Fe (mg/L) | Total Mercury (mg Hg/L) | Diss. Pb (mg/L) | Total Mn (mg/L) | Diss. Ni (mg/L) | Total Ni (mg/L) | Total Se (mg/L) | Diss. Zn (mg/L) | Total Zn (mg/L)
1Argo Tunnel (Denver, CO) | 250 | 550 | 2.0 - 3.0 | 2,500 - 3,750 |  | 1,000 - 3,000 | 15 - 35 | 0.02 - 0.3 | 0.05 - 0.3 | 4.0 - 7.0 | 75 - 200 | 0.005 - 0.15 | 65- 150 | 0.15 - 0.35 | 25 - 50 | 250 | 6.5 - 9.0 |  |  |  |  | 1 | 0.05 | 0.003 |  | 0.017 |  |  | 1 |  | 0.0016 | 1 | 0.059 |  |  | 0.125
1Eagle Mine (Eagle County, CO) | 400 | 450 | 5.1 |  | 70 | 4000 |  |  | 0.25 | 1.08 | 320 | 0.07 | 300 | n/a | 130 | 400 | 6.5 - 9.0 |  | 20 |  |  |  |  | 0.008 |  | 0.15 |  |  | 9.8 |  | 0.12 | 31 |  |  |  | 0.4
1Leadville Mine Drainage Tunnel (Leadville, CO) | 1600 | 2000 | 5.9 |  |  | 370 |  |  | 0.02 | n/a | 1.4 | n/a | 1.8 | n/a | 3.6 | 1600 | 6.5 - 9.0 | [6 empty] | 0.0044 |  |  |  |  | 1 |  |  | 1 |  |  |  | 0.127
2Golden Sunlight Mine (Whitehall, MT) | 400 | 400 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 400 | n/a |  | n/a | n/a |  | n/a | n/a | n/a |  | n/a |  |  | n/a |  | n/a | n/a | n/a |  |  | n/a
3Tyrone Mine (Tyrone, NM) | 1583 | 2563 | 3.41 - 3.96 | 3366 |  | 2131 | 122 | 0.018 | 0.116 | 282 | 17.9 | 0.092 | 16.5 | 6.95 | 29.9 | 1583 | n/a |  | n/a | <600 |  | n/a | n/a | n/a |  | n/a |  |  | n/a |  | n/a | n/a | n/a |  |  | n/a
4Landusky Mine (Fort Bellknap, MT) | 600 | 700 | 4.6 | 1688 |  | 1167 | 18 | <0.1 | 0.102 | 0.577 | 0.107 | <0.03 | 11.17 |  | 3.79 | 600 | 6.0 - 9.0 |  | 20 |  | 10 | 0.087 | 0.018 |  | 0.005 |  | 0.031 | 0.0052 | 1 | 5e-05 |  |  |  | 0.1 | 0.005 |  | 0.388
4Zortman Mine (Fort Bellknap, MT) | 175* | 1000 | 2.9 | 4085 |  | 3002 | 268 | 0.11 | 0.557 | 8.7 | 140 | <0.03 | 18.7 |  | 5.8 | 175 | 6.0 - 9.0 |  | 20 |  | 10 | 0.087 | 0.018 |  | 0.005 |  | 0.031 | 0.0052 | 1 | 5e-05 |  |  |  | 0.1 | 0.005 |  | 0.388
n/a = not available
* This plant is operated intermitently, approximately 1 week/month.
|  |  | Capital Costs |  |  | Annual Operating Costs |  |  |  | Summary
Facility | Treatment Method | Design Capacity (gpm) | Treatment Plant Construction | Other Treatment Related Facilities | Replacement costs | O&M Labor | O&M General Operations | Reagent Cost | Sludge Disposal | Subtotal Capital Costs | Subtotal Annual Operating Costs | Cost / 1000 gallon treated**
1Argo Tunnel (Denver, CO) | Sodium hydroxide precipitation | 700 | 5000000 |  |  | 410000 | 310000 | 269000 | $45/ton* | 5000000 | 989000 | 23.956
1Eagle Mine (Eagle County, CO) | Calcium hydroxide precipitation | 200 | 600000 |  |  | 400000 | 80000 | 276000 | $15/cy* | 600000 | 756000 | 3.39
1Leadville Mine Drainage Tunnel (Leadville, CO) | CO2 stripping, NaOH precipitation | 2000 | 7500000 |  |  | 182000 | 398000 | 220000 | $50/cy* | 7500000 | 800000 | 5.1875
2Golden Sunlight Mine (Whitehall, MT) | Calcium hydroxide precipitation | 400 | 475000 | 72868 | 828524 | 127572 | 260864 | 239919 |  | 1376392 | 628355 | 5.0119
3Tyrone Mine (Tyrone, NM) | Calcium hydroxide precipitation | 2563 | 15504999 | 4217386 | 2664806 | 303040 | 1025485 | 458035 |  | 22387191 | 1786560 | 15.2708
4Landusky Mine (Fort Bellknap, MT) | Calcium hydroxide precipitation, ferric sulfate and floc. precipitation | 600 | 2503250 |  | 3086624 | 259161.3145 | 236566.0023 | 18047.0475 | 20724.4155 | 5589874 | 534498.7798 | 10.2073
4Zortman Mine (Fort Bellknap, MT) | Calcium hydroxide precipitation, ferric sulfate and floc. precipitation | 2000 | n/a |  | n/a | 104137.4605 | 143690.3502 | 93316.995 | 5699.8095 | 0 | 346844.6152
*Cost included in O&M General Operations.
**Based on average treatment rate.
Average Cost |  | 10.5039 | /1000 gals treated
Construction Cost |  | 6534.916 | /gpm
Annual Operating Cost |  | 1136.8537 | /gpm
References:
1Willow M, tenBrack C. 1999. Survey of three hard-rock acid draininage treatment facilities in Colorado. Tailings and Mine Waste '99. pp 759-767. Based on actual costs.
2Hydrometrics, Inc. May 20, 1998. Estimated capital and operating costs for long-term water treatment at the Golden Sunlight Mine.
3NMED. 2001. Water treatment cost estimation prepared by Mark Phillip.
4Werner, Peter. 24 July 2000. Molycorp's Questa Mine Water Treatment Plan Cost Estimate. AND Bill Maehl personal communication 21 March 2003. AND Zortman and Landusky MPDES permits November 2001